REQUEST FOR COMMISSIONING SERVICES

NWQ Children's Center Renovation

University of Wisconsin - Milwaukee

DFD Project No. 11C2L

FOR The STATE OF WISCONSIN

Department of Administration, Division of Facilities dEVELOPMENT

State Administration Building, 101 East Wilson Street

Madison, WISCONSIN 53703

PROJECT INFORMATION

The Northwest Quadrant (NWQ) portion of the campus at the University of Wisconsin - Milwaukee is the former Columbia St. Mary’s Hospital. The NWQ building addresses are 1930 E. Hartford Ave (NWQ Building C) and 2015 E. Newport Ave. (NWQ Building D).

The work area on the Ground Floor is 29,615 Gross Square Feet (GSF) and the First Floor is 25,327 GSF, for a total of 54,942 GSF Square Feet. The project generally consists of the selective interior demolition of the ground and first floors of the C and D buildings on the NWQ, interior Architectural elements along with Plumbing, Mechanical and Electrical systems will be removed and the spaces will be improved for the relocation of the University’s Children Center. On other floors including the basement and 2nd floor, several Mechanical and Control systems will be upgraded and Air Handling Units will be removed and replaced.  The project also includes Div 21 fire protection scope and site work including two play areas totaling 25,300 sf (8,200 sf north and 17,100 sf south).

Several other NWQ projects are ongoing and include but are not limited to the following. Some** will require review and coordination with 11C2L:

DFD (DSF) Project No. 10D1M WALMS – CSM Hospital Site (NWQ Buildings A-F)**

DFD (DSF) Project No. 10D2Q Kenwood IRC/ Greenhouse (NWQ Buildings B & C)**

DFD (DSF) Project No. 11A3M UWM NWQ Central Utility Extension

DFD (DSF) Project No. 11E1B NWQ Parking Ramp Repair (NWQ Building G)

DFD (DSF) Project No. 11H3Y Roof Re-Coat (NWQ Building B Areas 5-9)

DFD (DSF) Project No. 11K3C NWQ Redevelopment Pre-design (NWQ Buildings A-F)

DFD (DSF) Project No. 12A1A NWQ Multi Building Elevator Renovation Upgrade (NWQ Buildings B &D)

DFD (DSF) Project No. 12B1R NWQ Telecom, Fire Alarm, Security System Upgrade (NWQ Buildings A-E)**

TBD Exterior Envelope (NWQ Buildings A-D & F)

TBD Elevator Upgrade (NWQ Building B - Red)

TBD Roofs (NWQ Building F)

Special commissioning requirements are to include LEED for Commercial Interiors v.2009 certification (LEED-CI Silver minimum, Gold goal) and DFD (DSF) Sustainable Requirements (LEED-NC silver equivalency minimum as it applies to the project).

Meeting the requirements of LEED CI credits includes, Energy and Atmosphere Prerequisite 1 Fundamental commissioning of Building Energy Systems and Energy and Atmosphere Credit 2 enhanced Commissioning.  Enhanced commissioning for LEED-CI requires:

       The CxA must report results, findings and recommendations directly to the owner.

        The CxA must conduct, at a minimum, 1 commissioning design review of the owner’s project requirements, basis of design and design documents prior to the mid-construction documents phase and must back-check the review comments in the subsequent design submission.

        The CxA must review contractor submittals applicable to systems being commissioned for compliance with the owner’s project requirements and basis of design. This review must be concurrent with the reviews of the architect or engineer of record and submitted to the design team and the owner.

        The CxA or other project team members must develop a systems manual that gives future operating staff the information needed to understand and optimally operate the project’s commissioned systems.

        The CxA or other project team members must verify that the requirements for training operating personnel and building occupants have been completed.

        The CxA must be involved in reviewing the operation of the tenant space with operations and maintenance (O&M) staff and occupants within 8 to 10 months after substantial completion. A plan for resolving outstanding commissioning-related issues must be included.

The owner’s project requirements are described in the 35% Design Report for DFD (DSF) Project No. 11C2L.

The construction estimate is $ 9,275,200 with total project budget of $ 11,981,000.

Proposed Schedule

Start of Design:			December 2011

Start of Construction 			March, 2013

Substantial Completion		November, 2013

Move in/occupancy			December, 2013

Project Design Team

Design team includes, all of Milwaukee, WI, prime A/E QUORUM ARCHITECTS and primary subconsultants ONE SOURCE CONSULTING Inc. (Civil), STRUCTURAL DIMENSION, RING & DU CHATEAU LLC (Mechanical/Electrical), and PSJ ENGINEERING Inc. (Plumbing/Fire Protection). Type 2 EIA was completed by Cornerstone Environment of Madison, WI.

COMMISSIONING SERVICES

Commissioning services will be in accordance with DFD (DSF) Policy and Procedure Manual for A/E and Consultants, Section Two - Commissioning.  The intent is to verify that systems and equipment are installed and performs according to the owner’s project requirements, basis of design, and construction documents and that the building operator has received equipment and systems documentation and training.

The commissioning services provider (CxP) will be independent of the design team and will report directly to DFD.

DFD expects commissioning services to commence at prior to construction phase.

Scope of commissioning activities and commissioned systems are indicated on the two attached tables.

Deliverables

Distribute the Commissioning Report as one hard copy and one electronic copy in pdf format to DFD, the Agency and A/E.

LETTER OF INTEREST

Proposed commissioning team:  Identify who will be providing commissioning services, their roles and any sub consultants.

Qualifications:  Provide documentation of expertise, qualifications and descriptions of relevant past projects for the consulting firm and for the individual(s) who will be performing the services.

Agency Contact: Karen Wolfert, email wolfertk@uwm.edu

Select items to be included within the project commissioning scope.

COMMISSIONING ACTIVITIES / SERVICES

The following activities correspond to DFD’s Commissioning policy and procedures that can be found in Section Two of the Policy and Procedure Manual for A/E and Consultants.  Reference the manual for a more detailed description of the required services.

| Commissioning Requirement | Cx Policy Reference | Table 2.1 & 2.2 Ref. |
| --- | --- | --- |
| Design Phase |
|  | Review Basis of Design/Design Concept to evaluate if construction documents meet Owner’s Project Requirements and DFD (DSF) guidelines. | 2.E.2.a | 4. |
|  | Provide input to A/E for inclusion in the Construction Verification Checklists and Functional Performance Test forms into the project manual. | 2.E.2.b | 5. |
|  | Review Preliminary Design documents to evaluate and comment on the design meeting the Owner’s Project Requirements and project goals. | 2.E.2.b | 5. |
|  | Review Final Design documents to ensure incorporation of preliminary review comments, elimination of construction ambiguities and completeness of the Construction Verification Checklists and Functional Performance Test forms. | 2.E.2.b | 5. |
|  | Review Bid documents for inclusion of DFD (DSF) & CxP comments. | 2.E.2.b | 5. |
|  | Develop a Commissioning Plan identifying the commissioning team, procedures, system tests, test sampling, milestones and responsibilities. | 2.E.2.c | 8. |
| Construction Phase |
|  | Attend and participate in the Construction Progress Meetings and lead the commissioning team of contractors and consultants. Provide Commissioning Plan overview at the Pre-construction Conference. | 2.E.3.a/c | 10. |
|  | Review Contractor’s Quality Control Plan, comment to DFD and incorporate into the Commissioning Plan. | 2.E.3.a | 9. |
|  | Conduct regularly scheduled Commissioning Meetings and regularly update the Commissioning Plan tracking status and responsibilities. | 2.E.3.d | 9. |
|  | Enter construction, functional performance, design discrepancies, etc. into the WisBuild Issues List. Track the issues to help move the issue to correction. When Contractor, A/E or DSF indicates an issue is corrected, verify and close the issue within WisBuild. | 2.E.3.e | 11. |
|  | Perform field checks of the Contractor completed Construction Verification Checklists. Enter non-conformance items into the Issues List. If there is more than a 10% deficiency, Contractor to correct and CxP to recheck. | 2.E.3.f | 12. |
|  | Establish sampling protocol for Functional Performance Testing. Witness, record and document the testing and report any deficiencies on the Issues List. | 2.E.3.g | 13. |
|  | Review HVAC testing, adjusting and balancing report, field verify with contractor, report deficiencies on the Issues List, track issues to resolution, verify corrections and close the Issues. | 2.E.3.h | 14. |
|  | Review Operations and Maintenance Manuals and provide comments to the A/E so they can include with the A/E’s review comments. | 2.E.3.i | 16. |
|  | Attend Agency training sessions, provide and collect attendee evaluation forms and evaluate training to ensure Agency training is adequate. | 2.E.3.k | 19. |
|  | Complete draft Commissioning Report and distribute to DSF, A/E, Contractors and Agency Contact. | 2.E.4.a | 19. |
| Post Construction Phase |
|  | Witness the Seasonal Functional Performance Testing, document the results and enter deficiencies into the Issues List and provide follow-up through closure. | 2.E.4.c | 23. |
|  | Within 10 months of substantial completion coordinate and facilitate a substantial completion review meeting and document findings to complete the final commissioning report. | 2.E.4.d | 22. |
|  | Complete final Commissioning Report and distribute to DSF, A/E and Agency Contact. | 2.E.4.c | 21. |
| Optional Commissioning Activities/Services |
|  | Complete an Energy Modeling Review | 2.E.4.d | 24. |
|  | Complete a M&V One-Year Report | 2.E.4.d | 24. |
|  | Complete Systems Manual | 2.E.3.j | 17. |

COMMISSIONED SYSTEMS - The following systems will be commissioned:

Edit the following list with input from DSF specialists and the Agency Contact.

| Divisions 3 thru 14 - General Construction |  | Boilers and Fuel Fired Equipment |
| --- | --- | --- |
|  | Concrete |  | Boiler Feedwater and Blowdown Systems |
|  | Masonry |  | Terminal Units |
|  | Waterproofing |  | Fan Coils, Unit Ventilators, Unit Heaters |
|  | Thermal Protection |  | Energy Recovery Systems |
|  | Building Envelope Sealing and Infiltration |  | Humidifiers |
|  | Roofing |  | Smoke Control Systems |
|  | Doors and Windows |  |  |
|  | Division 11 Equipment |  |  |
|  | Division 13 Equipment |  |  |
|  | Elevator (? color?) | Division 26 thru 28– Electrical |
|  |  |  | Lighting and Daylighting Controls* |
|  |  |  | Lighting Fixtures and Contactors |
|  |  |  | Exterior Site Lighting and Controls |
| Division 21 - Fire Suppression |  | Conductors, Conduit, Raceway and Cable Tray |
|  | Sprinkler and Standpipe Systems |  | Grounding and Bonding |
|  | Fire Pumps and Controls |  | Switchboards and Panelboards |
|  |  |  | Motor Starters and Motor Control Centers |
|  |  |  | Disconnect Switches and Circuit Breakers |
|  |  |  | Wiring Devices, Switches, Receptacles, Etc. |
| Division 22 - Plumbing |  | Generators and Transfer Switches |
|  | Domestic Water Systems |  | Metering |
|  | Domestic Hot Water Systems* |  | Surge Protective Devices |
|  | Plumbing Equipment |  | Transformers |
|  | Plumbing Fixtures |  | Unit Substations |
|  | Lab and Healthcare Gas and Vacuum Systems |  | Medium Voltage Switchgear |
|  | Laboratory and Healthcare Pure Water Systems |  | Medium Voltage Cable |
|  | Fuel Piping Systems |  | Fire Alarm Systems |
|  | Solar Thermal Systems |  | Communication Cabling, Outlets and Equipment |
|  | Food Service Equipment |  | Audio/Visual Systems |
|  | Swimming Pool Equipment |  | Access Control Systems |
|  |  |  | Video Surveillance Systems |
|  |  |  | Nurse Call Systems |
|  |  |  | Solar Photovoltaic Systems |
| Division 23 – HVAC* |  |  |
|  | Temp. Control & Building Automation Systems* |  |  |
|  | Testing and Balancing |  |  |
|  | Variable Frequency Drives | Divisions 32 & 33 – Exterior Improvements & Utilities |
|  | Piping Systems, Valves and Specialties |  | Soil Preparation, Seeding and Plantings |
|  | Pumps |  | Bioretention and Bioinfiltration Systems |
|  | Ductwork, Duct Accessories and Casing Systems |  | Correctional Fencing |
|  | Air Inlets and Outlets |  | Water Distribution Systems |
|  | Filtration |  | Sanitary Sewer and Storm Drainage Systems |
|  | Coils and Heat Exchangers |  | Steam and Condensate Systems |
|  | Fans and Air Handlers |  | Chilled Water and Hot Water Systems |
|  | Compressors and Condensing Units |  | Fuel Storage and Distribution Systems |
|  | Chillers and Cooling Towers |  | Geothermal Well Systems |
|  | Computer Room Air Conditioning Equipment |  | Renewable Energy Systems* |
|  | Heat Pumps |  | Playground |
|  | Dry Coolers and Heat Rejection Equipment |  | Underground Stormwater Storage |

Systems followed by an asterisk (*) are required to be commissioned in LEED® projects.

02/08/2011 G:\Bureau_of_Architecture_Engineering\Commissioning\Update2011CxReqSer\RequestForCommissiongServices02/08/2011.doc